## Terms
Standard Terms
Term | Definition
Circulation (Pump) | A pump within the plant that circulates a fluid through an individual piece of equipment such as a chiller, boiler, cooling tower or heat exchanger.
Command | Indicates a piece of equipment, valve, damper or fan has been command to a Boolean value of on/off or open/close. (See Enabled, Status and Position for related points)
Effective | Indicates the current temperature or pressure setpoint target given the current mode of operation. For a temperature or flow set point this value would change as a piece of equipment moves between occupied and unoccupied and heating and cooling modes.
Enabled | A Boolean software point indicating a piece of equipment is in or out of service and is available or not available to be commanded on or off. It does not indicate a piece of equipment is running or not running. Enabled should never be used to indicate the commanding of a point or piece of equipment on or off. Commonly used to take a piece of equipment out of service for maintenance or repair. Control logic will ignore equipment that is not enabled. (See Command and Status for related points)
Energy | Tracks the consumption of a unit of energy (kWh, MMbtu, etc.). Always an accumulated value with a hisTotalized tag.
Exhaust | Indicates undesired air leaving the building due to contaminants or other undesirable components like excess heat or humidity. Common areas would include mechanical areas, dryers, pools and laboratories.
History Intervals | Numeric history intervals for new projects with newer controlers and adequate memory should be 10 minutes. Retrofit work should coorespond with the existing intervals. In all cases the history interval should be the same for all points on a piece of equipment so that histories align on the same time boundareis.
Frequency | Frequency is a numeric value either commanding or sensing a VFD running at a specific Hz. See Speed for VFD percent control.
Loop (Pump) | A pump that distributes a fluid to a larger area such as a campus, district or building for end equipment use.
Mixed Air Damper | Mixed air damper should only be used when there is a specific third damper controlling mixed air separate from the the outside air damper and the return air damper. A two damper configuration of outside and return air dampers should never name one of the dampers as a mixed air damper.
Mode | A software point indicating the current operating intent of a piece of equipment. Used to understand the current system mode (i.e. Occupancy, Dehumidifing, Economizing, IAQ, etc.) when analyzing related points.
Occupancy | A Boolean point indicating a unit is in occupied or unoccupied mode.
Phase | Indicates electrical attributes (amps, volts, power or energy) as measured across an individual phase. A string value containing A, B, C, AB, BC, AC, AN, BN, CN.
Power | Tracks the instantaneous value of power (kW, MMbtu/h, etc.).
Position | A numeric value indicating a valve or damper open position between 0 and 100%.
PreHeat | Preheat indicates heating coils and valves intended to heat outside air to prevent the freezing of cooling coils. Often seen in cold climates with minimum outside air damper positions or large outside air requirements.
Primary | The primary tag is always used in the context of the site. Primary refers to piping, valves, pumps and sensors within the central plant that moves water between equipment in the plant. Common primary equipment includes individual chillers, boilers, heat exchangers, isolation valves, pumps and sensors.
Relief | Indicates excess air leaving the building in order to maintain overall building static pressure and indoor air quality.
Room | This term should not be used. Use "Zone" instead.
Secondary | The secondary tag is always used in the context of the site. Secondary refers to equipment or points moving air or fluids away from a source to another area for use. Common sources may include chilled water or hot water plants within a building or a central or district plant on a campus. Common uses may include campus distribution of chilled water, hot water, or steam; or chilled, hot or domestic water loops within a building.
Space | This term should not be used. Use "Zone" instead.
Speed | A numeric value commanding a fan or pump to run at a percentage of capacity from 0 to 100 percent.
Status | A Boolean point indicating proof a commanded action happened. Typically based on a measure of flow (air, water, current) resulting from the commanded action. Status should never be used to indicate the commanding of a point on or off. (See Command and Enabled for related points)
Zone | Zone is the general term used to define any area served by a VAV, FCU or direct zone AHU. The term “Room” or "Space" should not be used.
Total | Indicates the total power or energy across all phases of electricity.

## Abbreviations
Standard Abbreviations
Term | Abbreviation
Building Loop Pumps | P
Carbon Dioxide | CO2
Chilled Water | ChW
Chilled Water System | CHWS
Command | Cmd
Condenser Water | CW
Circulation Pump (individual equipment) | CP
Damper | Dmpr
Domestic Hot Water System | DHW
Enable | Enab
Entering | E
Frequency | Freq
Heat Exchanger | Hx
Hot Water | HW
Hot Water System | HWS
Leaving | L
Load | Load
Mechanical | Mech
Mixing | Mix
Occupancy/Occupied | Occ
Position | Pos
Power Factor | PF
Pre-Heat | PreHeat
Pressure | Press
Primary | Pri
Re-Heat | ReHeat
Setpoint | Sp
Speed | Spd
Static Pressure | Press
Status | Sts
Temperature | Temp
Valve | Vlv
Variable Frequency Drive | VFD
UnOccupied | Unocc
Water | Wtr

## AHU
AHU | With Return Air | equip, hvac, ahu, [rooftop], [mau], [elecHeat, hotWaterHeat, steamHeat, gasHeat, noHeat], [chilledWaterCool, dxCool, noCool], [directZone, vavZone, chilledBeamZone, multiZone], [singleDuct, dualDuct, tripleDuct], [hotDeck, coldDeck, neutralDeck], [constantVolume, variableVolume] [humidifier, noHumidifier], hotWaterPlantRef, chilledWaterPlantRef (plant?)
Description | Point Name navName | Tags | Point Type | UoM | History
General Points
Occupied Mode | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24hr
Building Static Pressure | BldgPress | building, air, pressure, sensor | Num, .01 | in w.c. | Int, 10 min
Building Static Pressure Setpoint | BldgPressSp | building, air, pressure, sp | Num, .01 | in w.c. | COV, 24hr
Filters
Filter Status | FilterSts | filter, run, sensor | Bool | Ok/Dirty | COV, 24hr
Filter Pressure Delta | FilterPressDelta | filter, pressure, delta, sensor | Num, .01 | in w.c. | Int, 10 min
Single Direct Zone Points
Zone CO2 | ZoneCO2 | zone, co2, sensor | Num, 0 | ppm | Int, 10min
Zone CO2 Setpoint | ZoneCO2Sp | zone, co2, sp, hisMode:cov | Num, 0 | ppm | COV, 24hr
Zone Pressure | ZonePress | zone, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min
Zone Pressure Setpoint | ZonePressSp | zone, air, pressure, sp, hisMode:cov | Num, .01 | in w.c. | COV, 24hr
Zone Temperature | ZoneTemp | zone, air, temp, sensor | Num, 1 | F | Int, 10min
Zone Temperature Setpoint (effective) | ZoneTempSp | zone, air, temp, effective, sp | Num, 0 | F | Int, 10min
Occupied Cooling Setpoint | OccCoolSp | occ, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Occupied Heating Setpoint | OccHeatSp | occ, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Cooling Setpoint | UnoccCoolSp | unocc, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Heating Setpoint | UnoccHeatSp | unocc, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Discharge Air Points - VAV Zones
DA Fan Command (single or common) | DaFanCmd | discharge, air, fan, run, cmd | Bool | On/Off | COV, 24hr
DA Fan Status (single or common) | DaFanSts | discharge, air, fan, run, sensor | Bool | On/Off | COV, 24hr
DA Fan Speed (single or common) | DaFanSpd | discharge, air, fan, speed, cmd | Num, 0 | % | Int, 10min
DA Fan Frequency (single or common) | DaFanFreq | discharge, air, fan, freq, sensor | Num, 0 | Hz | Int, 10min
DA Humidity | DaHumidity | discharge, air, humidity, sensor | Num, 0 | % | Int, 10min
DA Pressure | DaPress | discharge, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min
DA Pressure Setpoint | DaPressSp | discharge, air, pressure, sp, hisMode: cov | Num, .01 | in w.c. | Int, 10min
DA Temp | DaTemp | discharge, air, temp, sensor | Num, 1 | F | Int, 10min
DA Temp Setpoint | DaTempSp | discharge, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Systems with Return Air
RA CO2 | RaCO2 | return, co2, sensor | Num, 0 | ppm | Int, 10min
RA CO2 Setpoint | RaCO2Sp | return, co2, sp, hisMode:cov | Num, 0 | ppm | COV, 24hr
RA Damper Position | RaDmprPos | return, air, damper, cmd | Num, 0 | % | Int, 10min
RA DeHumidify Setpoint | RaDehumidSp | return, air, humidity, deHumidify, sp, hisMode:cov | Num, 0 | %RH | COV, 24hr
RA Humidify Setpoint | RaHumidSp | return, air, humidity, humidify, sp, hisMode:cov | Num, 0 | %RH | COV, 24hr
RA Humidity | RaHumidity | return, air, humidity, sensor | Num, 0 | %RH | Int, 10 min
RA Fan Command (single or common) | RaFanCmd | return, air, fan, run, cmd | Bool | On/Off | COV, 24hr
RA Fan Status (single or common) | RaFanSts | return, air, fan, run, sensor | Bool | On/Off | COV, 24hr
RA Fan Speed (single or common) | RaFanSpd | return, air, fan, speed, cmd | Num, 0 | % | Int, 10 min
RA Fan Frequency (single or common) | RaFanFreq | return, air, fan, freq, sensor | Num, 0 | Hz | Int, 10min
RA Pressure | RaPress | return, air, pressure, sensor | Num, .01 | in w.c. | Int, 10min
RA Pressure Setpoint | RaPressSp | return, air, pressure, sp | Num, .01 | in w.c. | COV, 1hr
RA Temp | RaTemp | return, air, temp, sensor | Num, 1 | F | Int, 10min
Systems with Relief Air
Relief Air Damper Position | RlfDmprPos | relief, air, damper, cmd | Num, 0 | % | Int, 10 min
Systems with Outside Air
Outside Air Damper Command (open/closed) | OaDmprCmd | outside, air, damper, cmd | Bool | Open/Closed | COV, 24hr
Outside Air Damper Position | OaDmprPos | outside, air, damper, cmd | Num, 0 | % | Int, 10 min
Outside Air Flow | OaFlow | outside, air, flow, sensor | Num, 0 | cfm | Int, 10 min
Outside Air Humidity | OaHumidity | outside, air, humidity, sensor | Num, 0 | %RH | Int, 10 min
Outside Air Temperature | OaTemp | outside, air, temp, sensor | Num, 1 | F | Int, 10 min
Mixed Air Points
Mixed Air Temp | MaTemp | mixed, air, temp, sensor | Num, 1 | F | Int, 10min
Mixed Air Damper Position | MaDmprPos | mixed, air, damper, cmd | Num, 0 | % | Int, 10min
Systems with Heating
Hot Water Circulation Pump Command | HWCPCmd | hot, water circ, pump, run, cmd | Bool | On/Off | COV, 24hr
Hot Water Circulation Pump Status | HWCPSts | hot, water circ, pump, run, sensor | Bool | On/Off | COV, 24hr
Hot Water Valve Position | HWVlvPos | hot, water, valve, cmd | Num, 0 | % | Int, 10min
Preheat Valve Position | PreheatVlvPos | preHeat, water, valve, cmd | Num, 0 | % | Int, 10min
Heating Coil Air Leaving Temp | HCALTemp | heat, air, temp, leaving, sensor | Num, 1 | F | Int, 10min
PreHeat Coil Air Leaving Temp | PreHCALTemp | preHeat, air, temp, leaving, sensor | Num, 1 | F | Int, 10min
Systems with Cooling
Chilled Water Pump Command | ChWCPCmd | chilled, water, pump, run, cmd | Bool | On/Off | COV, 24hr
Chilled Water Pump Status | ChWCPSts | chilled, water, pump, run, sensor | Bool | On/Off | COV, 24hr
Chilled Water Valve Position | ChWVlvPos | chilled, water, valve, cmd | Num, 0 | % | Int, 10min
Chiller Water Valve Status | ChWVlvSts | chilled, water, valve, run, sensor | Num, 0 | % | Int, 10min
Chiller Water Temp Entering | CHWEtemp | chilled, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Chiller Water Temp Leaving | CHWLtemp | chilled, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Chilled Water Flow | CHWFlow | chilled, water, flow, sensor | Num, 0 | gpm | Int, 10min
Cooling Coil Air Leaving Temp | CCALTemp | cool, air, temp, leaving, sensor | Num, 1 | F | Int, 10min
Cooling Coil Air Leaving Humidity | CCALHumidity | cool, air, humidity, leaving, sensor | Num, 1 | F | Int, 10min
Systems that Economize
Economize Mode | EconomizeMode | economize, run, cmd | Bool | Active/Inactive | COV
Systems that Humidify
Humidifier Enable | HumidifierEnab | humidifier, enable, cmd | Bool | Enabled/Disabled | COV
Humidifier Command | HumidifyCMD | humidifier, run, cmd | Bool | On/Off | COV
See Return Air Humidity & Humidify Setpoint
Systems that Dehumidify
DeHumidify Mode | DeHumidifyMode | deHumidify, run, cmd | Bool | Active/Inactive | COV
See Return Air Humidity & Dehumidify Setpoint
Energy Points - Heat Recovery Water |  | equip, water, meter, hru
Heat Recovery Water Temp Entering | HRUWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Temp Leaving | HRUWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Volumertic Flow | HRUWFlow | water, flow, sensor | Num, 1 | gal/min | Int, 10min
Heat Recovery Water Energy (accumulated) | HRUWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min
Heat Recovery Water Power | HRUWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Heat Recovery Pump Command | HRUCPCmd | hru, circ, pump, run, cmd | Bool | On/Off | COV, 24hr
Heat Recovery Air Leaving Temp | HRUALTemp | hru, air, temp, leaving, sensor | Num, 1 | F | Int, 10min

## FCU
FCU |  | equip, hvac, fcu, [elecHeat, hotWaterHeat, noHeat] [chilledWaterCool, noCool]
Description | Point Name navName | Tags | Point Type | UoM | History
Occupied Mode | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24hr
Chilled Water Valve | ChWVlvPos | chilled, water, valve, cmd | Num, 0 | % | Int, 10min
Discharge Air Temperature | DaTemp | discharge, air, temp, sensor | Num, 1 | F | Int, 10min
Fan Command | FanCmd | fan, run, cmd | Bool | On/Off | COV, 24hr
Fan Status | FanSts | fan, run, sensor | Bool | On/Off | COV, 24hr
Fan Speed | FanSpeed | fan, speed, cmd | enum | Off/Low/Med/High | COV, 24hr
Hot Water Valve | HWVlvPos | hot, water, valve, cmd | Num, 0 | % | Int, 10min
Zone Temperature | ZoneTemp | zone, air, temp, sensor | Num, 1 | F | Int, 10min
Zone Temperature Setpoint (effective) | ZoneTempSp | zone, air, effective, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Occupied Cooling Setpoint | OccCoolSp | occ, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Occupied Heating Setpoint | OccHeatSp | occ, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Cooling Setpoint | UnoccCoolSp | unocc, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Heating Setpoint | UnoccHeatSp | unocc, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
While the four occ/unocc heating/cooling setpoints above rarely change, their histories are needed in analytics to determine when temperatures have drifted too high or low.

## VAV
VAV |  | equip, vav, ahuRef, [fanPowered, series, parallel], [singleDuct, dualDuct], [hotWaterReheat, elecReheat, coolOnly]
Description | Point Name navName | Tags | Point Type | UoM | History
Occupied Mode | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24Hr
Discharge Air Flow | DaFlow | discharge, air, flow, sensor | Num, 0 | cfm | Int, 10min
Discharge Air Flow Setpoint | DaFlowSp | discharge, air, flow, effective, sp | Num, 0 | cfm | Int, 10min
Damper Position | DmprPos | air, damper, cmd | Num, 0 | % | Int, 10min
Reheat Valve | HWVlvlPos | reheat, water, valve, cmd | Num, 0 | % | Int, 10min
Discharge Air Temperature | DaTemp | discharge, air, temp, sensor | Num, 1 | F | Int, 10min
Zone Temperature | ZoneTemp | zone, air, temp, sensor | Num, 1 | F | Int, 10min
Zone Temperature Setpoint (effective) | ZoneTempSp | zone, air, temp, effective, sp | Num, 0 | F | COV, 24Hr
Occupied Cooling Setpoint | OccCoolSp | occ, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Occupied Heating Setpoint | OccHeatSp | occ, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Cooling Setpoint | UnoccCoolSp | unocc, cooling, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Unoccupied Heating Setpoint | UnoccHeatSp | unocc, heating, zone, air, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Zone Humidity | ZoneHumidity | zone, air, humidity, sensor | Num, 0 | %RH | Int, 10min
Zone Humidity Setpoint | ZoneHumiditySp | zone, air, humidity, sp | Num, 0 | %RH | Int, 10min
Zone CO2 | ZoneCO2 | zone, air, co2, sensor | Num, 0 | ppm | Int, 10min
Zone CO2 Setpoint | ZoneCO2Sp | zone, air, co2, sp | Num, 0 | ppm | Int, 10min
Optional Commissioning Points
Cooling Max Flow | CoolMaxFlow | cooling, max, flow, sp | Num, 0 | cfm | COV, 24hr
Cooling Min Flow | CoolMinFlow | cooling, min, flow, sp | Num, 0 | cfm | COV, 24hr
Heating Max Flow | HeatMaxFlow | heating, max, flow, sp | Num, 0 | cfm | COV, 24hr
Heating Min Flow | HeatMinFlow | heating, min, flow, sp | Num, 0 | cfm | COV, 24hr
Fan Powered Boxes
Fan Speed | FanSpeed | fan, speed, run, cmd | Num, 0 | % | Int, 10min
Fan High Speed | FanSpeedHigh | fan, speed, high, run, cmd | Bool | On/Off | COV, 24Hr
Fan Medium Speed | FanSpeedMed | fan, speed, med, run, cmd | Bool | On/Off | COV, 24Hr
Fan Low Speed | FanSpeedLow | fan, speed, low, run, cmd | Bool | On/Off | COV, 24Hr

## Chiller
Chiller |  | equip, chiller, chilledWaterPlantRef, [absorption, reciprocal, screw, centrifugal], [waterCooled, airCooled]
Description | Point Name navName | Tags | Point Type | UoM | History
Chiller Enable | ChrEnab | chiller, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Chiller Command | ChrCmd | chiller, run, cmd | Bool | On/Off | COV, 24hr
Chiller Status | ChrSts | chiller, run, sensor | Bool | On/Off | COV, 24hr
Condenser Water Isolation Valve | CWVlvCmd | condenser, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Condesner Water Circulation Pump | CWCPCmd | condenser, circ, pump, cmd | Bool | On/Off | COV, 24hr
Condenser Water Entering Temperature | CWETemp | condenser, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Condenser Water Leaving Temperature | CWLTemp | condenser, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Isolation Valve | ChWVlvCmd | chilled, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Chilled Water Entering Temperature | ChWETemp | chilled, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Leaving Temperature | ChWLTemp | chilled, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Setpoint | ChWSp | chilled, water, leaving, temp, sp, hisMode:cov | Num, 0 | F | COV, 24hr
Chilled Water Flow | ChWFlow | chilled, water, flow, sensor | Num, 0 | gal/min | Int, 10min
Oil Temp | ChrOilTemp | oil, temp, sensor | Num, 1 | F | Int, 10min
Oil Heater Command | ChrOilHeatCmd | oil, heater, run, cmd | Bool | On/Off | COV, 24hr
Oil Heater Status | ChrOilHeatSts | oil, heater, run, sensor | Bool | On/Off | COV, 24hr
Load | ChrLoad | load, sensor | Num, 0 | % | Int, 10min
Energy Points - Electric |  | equip, elec, meter, chiller
Tons | ChrTons | chilled, water, power, sensor | Num, 0 | tonref | 5 COV, 1hr
Current | ChrCurrent | mag, current, sensor | Num, 0 | A | 5 COV, 1hr
Volts | ChrVolts | volt, mag, sensor | Num, 0 | V | 5 COV, 1hr
Energy Total (accumulated) | ChrEnergy | elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
Power Total | ChrPower | elec, power, total, active, sensor | Num, 0 | kW | Int, 10min
Power Factor Total | ChrPF | pf, total, sensor | Num, 0.01 | unitless | Int, 10min
Energy Points - Water |  | equip, water, meter, chiller
Chilled Water Temperature Entering | ChWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min
Chilled Water Temperature Leaving | ChWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Chilled Water Flow | ChWFlow | water, flow, sensor | Num, 1 | gal/min | Int, 10min
Chilled Water Volume (accumulated) | ChWVolume | water, volume, total, sensor | Num, 0 | gal | Int, 10min
Chilled Water Energy (accumulated) | ChWEnergy | water, energy, hisTotalized, sensor | Num, 0 | btu | Int, 10min
Chilled Water Power | ChWPower | water, power, sensor | Num, 0 | btu/h | Int, 10min

## Boiler
Boiler |  | equip, boiler, hotWaterPlantRef, [condensing, automospheric] [hot water, steam] [oil, gas]
Description | Point Name navName | Tags | Point Type | UoM | History
Boiler Enable | BlrEnab | boiler, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Boiler Command | BlrCmd | boiller, run, cmd | Bool | On/Off | COV, 24hr
Boiler Status | BlrSts | boiller, run, sensor | Bool | On/Off | COV, 24hr
Entering Water Temperature | BlrETemp | entering, water, temp, sensor | Num, 1 | F | Int, 10min
Leaving Water Temperature | BlrLTemp | leaving, water, temp, sensor | Num, 1 | F | Int, 10min
Boiler Leaving Setpoint | BlrLTempSp | leaving, water, temp, sp | Num, 0 | F | COV, 24hr
Boiler Isolation Valve | BlrVlvCmd | isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Boiler Circulation Pump | BlrCPCmd | pump, circ, run, cmd | Bool | On/Off | COV, 24hr
Burner Level | BlrLevel | boiler, level, sensor | Num, 0 | % | Int, 10min
Systems with Heat Recovery
Heat Recovery Circulation Pump Command | HRUCPCmd | pump, circ, run, cmd | Bool | On/Off | COV, 24hr
Heat Recovery Circulation Pump Status | HRUCPSts | pump, circ, run, sensor | Bool | On/Off | COV, 24hr
Energy Points - Gas |  | equip, gas, meter, boiler
Gas Flow | BlrGasFlow | gas, flow, sensor | Num, 0 | ccf/h | Int, 10min
Gas Volume (accumulated) | BlrGasVolume | gas, volume, sensor, hisTotalized | Num, 0 | ccf | Int, 10min
Gas Energy (accumulated) | BlrGasEnergy | gas, energy, sensor, hisTotalized | Num, 0 | Mmbtu | Int, 10min
Gas Power | BlrGasPower | gas, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Energy Points - Water |  | equip, water, meter, boiler
Boiler Water Temperature Entering | BlrWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min
Boiler Water Temperature Leaving | BlrWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Boiler Water Flow | BlrWFlow | water, flow, sensor | Num, 1 | gal/min | Int, 10min
Boiler Water Volume (accumulated) | BlrWVolume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min
Boiler Water Energy (accumulated) | BlrWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min
Boiler Water Power | BlrWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Energy Points - Heat Recovery Water |  | equip, water, meter, boiler, hru
Heat Recovery Water Temp Entering | HRUWEtemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Temp Leaving | HRUWLTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Flow | HRUWFlow | water, flow, sensor | Num, 0 | gal/min | Int, 10min
Heat Recovery Water Volume (accumulated) | HRUWVolume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min
Heat Recovery Water Energy (accumulated) | HRUWEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min
Heat Recovery Water Power | HRUWPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min

## Fan
Fans (individual) |  | equip, fan
| Discharge Fan | equip, discharge, fan
| Return Fan | equip, return, fan
| Exhaust Fan | equip, exhaust, fan
| Relief Fan | equip, relief, fan
| FCU Fan | equip, fcu, fan
| Cooling Tower | equip, coolingTower, fan
Description | Point Name navName | Tags | Point Type | UoM | History
Fan Command | FanCmd | fan, run, cmd | Bool | On/Off | COV, 24hr
Fan Status | FanSts | fan, run, sensor | Bool | On/Off | COV, 24hr
Fan Speed | FanSpeed | fan, speed cmd, hisMode:cov | enum | Off/Low/Med/High | COV, 24hr
Fan VFD Speed | FanVFDSpd | fan, speed, cmd | Num, 0 | % | Int, 10min
Fan VFD Frequency | FanVFDFreq | fan, freq, sensor | Num, 0 | Hz | Int, 10min
VFD Energy Total (accumulated) | VFDEnergy | fan, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
VFD Power Total | VFDPower | fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min

## Pump
Pumps (individual) |  | equip, pump
| Chiller Circ Pump | equip, pump, chiller, circ, primary
| ChW Pump | equip, pump, chilled, secondary
| Boiler Circ Pump | equip, pump, boiler, circ, primary
| HW Pump | equip, pump, hot, secondary
| DHW Pump | equip, pump, domestic, hot
| GHW Pump | equip, pump, glycol, hot
| CT Pump | equip, pump, coolingTower
| CW Pump | equip, pump, condenser
Description | Point Name navName | Tags | Point Type | UoM | History
Pump Enable | PumpEnab | pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Pump Command | PumpCmd | pump, run, cmd | Bool | On/Off | COV, 24hr
Pump Status | PumpSts | pump, run, sensor | Bool | On/Off | COV, 24hr
Pump VFD Speed | PumpVFDSpd | pump, speed, cmd | Num, 0 | % | Int, 10min
Pump VFD Frequency | PumpVFDFreq | pump, freq, sensor | Num, 0 | Hz | Int, 10min
Energy Points - Electric |  | equip, elec, meter, pump
VFD Energy Total (accumulated) | VFDEnergy | pump, elec, energy, hisTotalized, sensor | Num, 0 | kWh | Int, 10min
VFD Power Total | VFDPower | pump, elec, power, active, hisTotalized, sensor | Num, 0 | kW | Int, 10min
Energy Points - Water |  | equip, water, meter, chiller
Water Temperature Entering | Etemp | water, temp, entering, sensor | Num, 1 | F | Int, 10min
Water Temperature Leaving | LTemp | water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Water Flow | Flow | water, flow, sensor | Num, 1 | gal/min | Int, 10min
Water Volume (accumulated) | Volume | water, volume, hisTotalized, sensor | Num, 0 | gal | Int, 10min
Water Energy (accumulated) | WtrEnergy | water, energy, hisTotalized, sensor | Num, 0 | MMbtu | Int, 10min
Water Power | WtrPower | water, power, sensor | Num, 0 | MMbtu/h | Int, 10min

## Electric
Electric Meter |  | equip, elec, meter, [siteMeter, submeterOf]
Description | Point Name navName | Tags | Point Type | UoM | History
Energy Points - Electric
Energy Total (accumulated) | Energy | elec, total, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
Power Total | Power | elec, total, power, active, sensor | Num, 0 | kW | Int, 10min
Power Factor Total | PF | elec, total, pf, sensor | Num, 0.01unitless | unitless | Int, 10min
Power Quality Points
Current A | Current_A | elec, phase, current, sensor | Num, 1 | A | Int, 10min
Current B | Current_B | elec, phase, current, sensor | Num, 1 | A | Int, 10min
Current C | Current_C | elec, phase, current, sensor | Num, 1 | A | Int, 10min
Volts AN | Volts_AN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Volts BN | Volts_BN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Volts CN | Volts_CN | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Volts AB | Volts_AB | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Volts BC | Volts_BC | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Volts CA | Volts_CA | elec, phase, volts, sensor | Num, 0 | V | Int, 10min
Power Factor A | PF_A | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min
Power Factor B | PF_B | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min
Power Factor C | PF_C | elec, phase, pf, sensor | Num, 0.01 | unitless | Int, 10min
Energy A (accumulated) | Energy_A | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
Energy B (accumulated) | Energy_B | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
Energy C (accumulated) | Energy_C | elec, phase, energy, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
Power A | Power_A | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min
Power B | Power_B | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min
Power C | Power_C | elec, phase, power, active, sensor | Num, 0 | kW | Int, 10min

## Gas
Gas Meter |  | equip, gas, meter, [siteMeter, submeterOf]
Description | Point Name navName | Tags | Point Type | UoM | History
Gas Flow | GasFlow | gas, flow, sensor | Num, 0 | ccf/h | Int, 10min
Gas Volume (accumulated) | GasVolume | gas, volume, sensor, hisTotalized | Num, 0 | ccf | Int, 10min
Gas Energy (accumulated) | GasEnergy | gas, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Gas Power | GasPower | gas, power, sensor | Num, 0 | MMbtu/h | Int, 10min

## CHWS
CHWS (Chilled Water System) |  | equip, chilledWaterPlant
Description | Point Name navName | Tags | Point Type | UoM | History
Chilled Water Flow | ChWFlow | chilled, flow, sensor | Num, 1 | gal/min | Int, 10min
Chilled Water Volume (accumulated) | ChWVolume | chilled, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Chilled Water Supply Temp | ChWSTemp | chilled, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Supply Temp Setpoint | ChWSTempSp | chilled, water, leaving, temp, sp | Num, 0 | F | COV, 24 hr
Chilled Water Return Temp | ChWRTemp | chilled, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Chilled Water Pressure Delta | ChWPressDelta | chilled, water, pressure, delta, sensor | Num, 0 | psi | Int, 10 min
Chilled Water Pressure Delta Setpoint | ChWPressDeltaSp | chilled, water, pressure, delta, sp | Num, 0 | psi | COV, 24 hr
Energy Points - Water |  | equip, water, meter, chilledWaterPlant, [siteMeter, submeterOf]
Chilled Water Temperature Entering | ChWEtemp | chilled, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Chilled Water Temperature Leaving | ChWLTemp | chilled, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Chilled Water Flow | ChWFlow | chilled, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Chilled Water Volume (accumulated) | ChWVolume | chilled, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Chilled Water Energy (accumulated) | ChWEnergy | chilled, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Chilled Water Power | ChWPower | chilled, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Chilled Water Building Loop Pumps |  | equip, chilled, water, pump, secondary
Building Loop Pump Enable | ChWPEnab | chilled, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Building Loop Pump Command | ChWPCmd | chilled, water, pump, run, cmd | Bool | On/Off | COV, 24hr
Building Loop Pump Status | ChWPSts | chilled, water, pump, run, sensor | Bool | On/Off | COV, 24hr
Building Loop Pump VFD Speed | ChWPVFDSpd | chilled, water, pump, speed, cmd | Num, 0 | % | Int, 10min
Building Loop Pump VFD Frequency | ChWPVFDFreq | chilled, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Building Loop Return Valve Command | ChWRetVlvCmd | chilled, water, return, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Building Loop Return Valve Sensor | ChWRetVlvSts | chilled, water, return, valve, sensor | Bool | On/Off | COV, 24hr
Energy Points - Electric |  | equip, elec, meter, chilled, water, pump, [siteMeter, submeterOf]
VFD Energy Total (accumulated) | ChWPVFDEnergy | chilled, water, pump, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
VFD Power Total | ChWPVFDPower | chilled, water, pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min
Chilled Water Heat Exchanger |  | equip, chilled, water, heatExchanger
Chilled Water Heat Exchanger Enabled | HxChWEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Chilled Water Heat Exchanger Command | HxChWCmd | run, cmd | Bool | On/Off | COV, 24hr
Chilled Water Heat Exchanger Runtime | HxChWRuntime | chilled, water, total, sensor | Num, 1 | h | Int, 10min
Chilled Water Entering Temperature | HxChWETemp | chilled, water, entering, temp | Num, 1 | F | Int, 10min
Chilled Water Leaving Temperature | HxChWLTemp | chilled, water, leaving, temp | Num, 1 | F | Int, 10min
Chilled Water Isolation Valve | HxChWVlvCmd | chilled, water, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Chilled Water Circulation Pump Command | HxChWCPCmd | chilled, water, circ, pump, run, cmd | Bool | On/Off | COV, 24hr
Chilled Water Circulation Pump Status | HxChWCPSts | chilled, water, circ, pump, run, sensor | Bool | On/Off | COV, 24hr
Condenser Water Entering Temperature | HxCWETemp | condenser, entering, water, temp | Num, 1 | F | Int, 10min
Condesner Water Leaving Temperature | HxCWLTemp | condenser, leaving, water, temp | Num, 1 | F | Int, 10min
Condesner Water Isolation Valve | HxCWVlvCmd | condenser, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
Condenser Circ Pump Command | HxCWCPCmd | condenser, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
Condenser Circ Pump Status | HxCWCPSts | condenser, water, circ, pump, sensor | Bool | On/Off | COV, 24hr

## HWS
HWS (Hot Water System) |  | equip, hotWaterPlant,
Description | Point Name navName | Tags | Point Type | UoM | History
Hot Water Flow | HWFlow | hot, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Hot Water Volume (accumulated) | HWVolume | hot, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Hot Water Supply Temp | HWSTemp | hot, water, leaving, temp, sensor | Num, 1 | F | COV, 15min
Hot Water Supply Temp Setpoint | HWSTempSp | hot, water, leaving, temp, sp | Num, 0 | F | COV, 24 hr
Hot Water Return Temp | HWRTemp | hot, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Hot Water Pressure Delta | HWPressDelta | hot, water, pressure, delta, sensor | Num, 1 | psi | Int, 10 min
Hot Water Pressure Delta Setpoint | HWPressDeltaSp | hot, water, pressure, delta, sp | Num, 1 | psi | COV, 24 hr
Energy Points - Water |  | equip, meter, hotWaterPlant, [siteMeter, submeterOf]
Hot Water Temperature Entering | HWEtemp | hot, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Hot Water Temperature Leaving | HWLTemp | hot, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Hot Water Flow | HWFlow | hot, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Hot Water Volume (accumulated) | HWVolume | hot, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Hot Water Energy (accumulated) | HWEnergy | hot, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Hot Water Power | HWPower | hot, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Building Hot Water Loop Pumps |  | equip, secondary, hot, water, pump,
Building Loop Pump Enable | HWPEnab | hot, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Building Loop Pump Command | HWPCmd | hot, water, pump, run, cmd | Bool | On/Off | COV, 24hr
Building Loop Pump Status | HWPSts | hot, water, pump, run, sensor | Bool | On/Off | COV, 24hr
Building Loop Pump VFD Speed | HWPVFDSpd | hot, water, pump, speed, cmd | Num, 0 | % | Int, 10min
Building Loop Pump VFD Frequency | HWPVFDFreq | hot, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Energy Points - Electric |  | equip, elec, meter, pump, hotWaterPlant, [siteMeter, submeterOf]
VFD Energy Total (accumulated) | HWPVFDEnergy | hot, water, pump, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
VFD Power Total | HWPVFDPower | hot, water, pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min

## DHW
Domestic Hot Water |  | equip, domestic, hotWaterPlant
Description | Point Name navName | Tags | Point Type | UoM | History
Water Flow | DHWFlow | domestic, hot, water, flow, sensor | Num, 0 | gal/min | Int, 10min
Water Volume (accumulated) | DHWVolume | domestic, hot, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Supply Temperature | DHWSTemp | domestic, hot, water, leaving, temp, sensor | Num, 1 | F | Int, 10min
Supply Temperature Setpoint | DHWSTempSp | domestic, hot, water, leaving, temp, sp | Num, 0 | F | Int, 10min
Return Temperature | DHWRTemp | domestic, hot, water, entering, temp, sensor | Num, 1 | F | Int, 10min
DHW Building Loop Pumps |  | equip, domestic, secondary, hot, water, pump
Building Loop Pump Enable | DHWPEnab | domestic, hot, water, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Building Loop Pump Command | DHWPCmd | domestic, hot, water, pump, run, cmd | Bool | On/Off | COV, 24hr
Building Loop Pump Status | DHWPSts | domestic, hot, water, pump, run, sensor | Bool | On/Off | COV, 24hr
Building Loop Pump VFD Speed | DHWPVFDSpd | domestic, hot, water, pump, speed, cmd | Num, 0 | % | Int, 10min
Building Loop Pump VFD Frequency | DHWPVFDFreq | domestic, hot, water, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Heat Exchanger |  | equip, domestic, hot water, heatExchanger
DHW Heat Exchanger Enabled | HxDHWEnab | domestic, enable, cmd | Bool | Enabled/Disabled | COV, 24hr
DHW Heat Exchanger Command | HxDHWCmd | domestic, run, cmd | Bool | On/Off | COV, 24hr
DHW Heat Exchanger Runtime | HxDHWRuntime |  | Num, 1 |  | Int, 10min
DHW Water Entering Temperature | HxDHWETemp | domestic, entering, water, temp, sensor | Num, 1 | F | Int, 10min
DHW Water Leaving Temperature | HxDHWLTemp | domestic, leaving, water, temp, sensor | Num, 1 | F | Int, 10min
DHW Water Isolation Valve | HxDHWVlvCmd | domestic, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
DHW Circulation Pump Command | HxDHWCPCmd | domestic, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
DHW Circulation Pump Status | HxDHWCPSts | domestic, water, circ, pump, sensor | Bool | On/Off | COV, 24hr
HWS Water Entering Temperature | HxHWSETemp | domestic, primary, entering, water, temp, sensor | Num, 1 | F | Int, 10min
HWS Water Leaving Temperature | HxHWSLTemp | domestic, primary, leaving, water, temp, sensor | Num, 1 | F | Int, 10min
HWS Water Isolation Valve | HxHWSVlvCmd | domestic, primary, isolation, valve, cmd | Bool | Open/Closed | COV, 24hr
HWS Circ Pump Command | HxHWSCPCmd | domestic, primary, water, circ, pump, cmd | Bool | On/Off | COV, 24hr
HWS Circ Pump Status | HxHWSCPSts | domestic, primary, water, circ, pump, sensor | Bool | On/Off | COV, 24hr
Energy Points - Water |  | equip, water, meter, domestic, hot
Domestic Hot Water Temperature Entering | DHWEtemp | domestic, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Domestic Hot Water Temperature Leaving | DHWLTemp | domestic, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Domestic Hot Water Flow | DHWFlow | domestic, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Domestic Hot Water Volume (accumulated) | DHWVolume | domestic, water, volume, sensor, hisTotalized | Num, 0 | gal | Int, 10min
Domestic Hot Water Energy (accumulated) | DHWEnergy | domestic, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Domestic Hot Water Power | DHWPower | domestic, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min
Energy Points - Heat Recovery Water |  | equip, water, domestic, meter, hru
Heat Recovery Water Temperature Entering | HRUWEtemp | domestic, water, temp, entering, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Temperature Leaving | HRUWLTemp | domestic, water, temp, leaving, sensor | Num, 1 | F | Int, 10min
Heat Recovery Water Flow | HRUWFlow | domestic, water, flow, sensor | Num, 1 | gal/min | Int, 10min
Heat Recovery Water Volume (accumulated) | HRUWVolume | domestic, water, volume, total, sensor | Num, 0 | gal | Int, 10min
Heat Recovery Water Energy (accumulated) | HRUWEnergy | domestic, water, energy, sensor, hisTotalized | Num, 0 | MMbtu | Int, 10min
Heat Recovery Water Power | HRUWPower | domestic, water, power, sensor | Num, 0 | MMbtu/h | Int, 10min

## EF
EF (Exhaust Fans) |  | equip, exhaust, fan
Description | Point Name navName | Tags | Point Type | UoM | History
Occupancy | Occ | occupied, cmd | Bool | Occ/UnOcc | COV, 24Hr
Exhaust Fan Enable | EFEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24hr
Exhaust Fan Command | EFCmd | fan, run, cmd | Bool | On/Off | COV, 24hr
Exhaust Fan Status | EFSts | fan, run, sensor | Bool | On/Off | COV, 24hr
Exhaust Damper Command (open/closed) | EFDmprCmd | damper, cmd | Bool | Open/Closed | COV, 24hr
Exhaust Damper Position | EFDmprPos | damper, cmd | Num, 0 | % | Int, 10min
Exhaust Damper Status | EFDmprSts | damper, sensor | Bool | On/Off | COV, 24hr
Energy Points - Electric |  | equip, elec, meter, exhaust, fan [siteMeter, submeterOf]
VFD Energy Total (accumulated) | EFVFDEnergy | exhaust, fan, elec, energy, total, sensor, hisTotalized | Num, 0 | kWh | Int, 10min
VFD Power Total | EFVFDPower | exhaust, fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min

## Cooling Tower
Cooling Tower |  | equip, coolingTower [openLoop, closedLoop]
Description | Point Name navName | Tags | Point Type | UoM | History
Cooling Tower Enabled | CTEnab | enable, cmd | Bool | Enabled/Disabled | COV, 24
Condenser Water Entering Temperature | CTCWETemp | condenser, water, entering, temp, sensor | Num, 1 | F | Int, 10min
Condenser Water Leaving Temperature | CTCWLTemp | condenser, water, leaving, temp sensor | Num, 1 | F | Int, 10min
Sump Temperature | CTSumpTemp | sump, temp, sensor | Num, 1 | F | Int, 10min
Sump Heater Command | CTSumpHtrCmd | sump, heating, run, cmd | Bool | On/Off | COV, 24
Sump Heater Status | CTSumpHtrSts | sump, heating, run, sensor | Bool | On/Off | COV, 24
Fan Enabled | CTFanEnab | fan, enable, cmd | Bool | Enabled/Disabled | COV, 24
Fan Command | CTFanCmd | ran, run, cmd | Bool | On/Off | COV, 24
Fan Status | CTFanSts | fan, run, sensor | Bool | On/Off | COV, 24
Fan VFD Speed | CTFanSpd | fan, speed, cmd | Num, 0 | % | Int, 10min
Fan VFD Freqency | CTFanVFDFreq | fan, freq, sensor | Num, 0 | Hz | Int, 10min
Pump Enabled | CTCPEnab | circ, pump, enable, cmd | Bool | Enabled/Disabled | COV, 24
Pump Command | CTCPCmd | circ, pump, run, cmd | Bool | On/Off | COV, 24
Pump Status | CTCPSts | circ, pump, run, sensor | Bool | On/Off | COV, 24
Pump VFD Speed | CTCPVFDSpd | circ, pump, speed, cmd | Num, 0 | % | Int, 10min
Pump VFD Frequency | CTCPVFDFreq | circ, pump, freq, sensor | Num, 0 | Hz | Int, 10min
Energy Points - Electric |  | equip, elec, meter, coolingTower, fan [siteMeter, submeterOf]
Fan VFD Energy Total (accumulated) | CTFanVFDEnergy | fan, elec, energy, total, sensor, hisTotalized | Num, 0 | KWh | Int, 10min
Fan VFD Power Total | CTFanVFDPower | fan, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min
Energy Points - Electric |  | equip, elec, meter, coolingTower, pump [siteMeter, submeterOf]
Pump VFD Energy Total (accumulated) | CTPVFDEnergy | pump, elec, energy, total, sensor, hisTotalized | Num, 0 | KWh | Int, 10min
Pump VFD Power Total | CTPVFDPower | pump, elec, power, total, active, sensor | Num, 0 | kW | Int, 10min